## Sheet1
# | Type | Equipment | Q’ty | Flange | Material | Communication Protocol* | Remarks
|  |  |  | Connection |  | [notes 1, 2]
1 | High & High High level indicators | Tank Alarms LAH (95%) & LAHH (98%) | 2 | 4" ANSI 150 | AISI 316 | Modbus RTU | -Float type (FT)
|  | MU1, MU2 alarm heights A (98%) 510 mm, B (95%) 730 mm |  |  |  | or | -distances A & B from flange face
Serial Interface RS-485 / TCP
2 | High & High High level indicators | Tank Alarms LAH (95%) & LAHH (98%) | 1 | 4" ANSI 150 | AISI 316 | Modbus RTU | -Float type (FT)
|  | MC3 alarm heights A (98%) 470 mm, B (95%) 650 mm |  |  |  | or | -distances A & B from flange face
Serial Interface RS-485 / TCP
3 | Low level indicators | Tank Alarms LAL (5%) | 2 | 2" ANSI 150 | AISI 316L | Serial Interface RS-485 | -rope probe
|  | MU1, MU2 alarm height C (5%) 4570 mm |  |  |  | or | -distance C from flange face
4-20 mA HART
4 | Low level indicators | Tank Alarms LAL (5%) | 1 | 2" ANSI 150 | AISI 316L | Serial Interface RS-485 | -rope probe
|  | MC3 alarm height C (5%) 3850 mm |  |  |  | or | -distance C from flange face
4-20 mA HART
5 | Level Gauging System | Marine level gauge, SUS 316 measuring drum with flexible multi-strand SUS 316 wire attached to float | 3 | 6" ANSI 150 | AISI 316L | Modbus | remote indicator required
|  | MU1, MU2, MC3 |  |  |  | or
Serial Interface RS-485 / TCP
6 | Non-intrusive Level Switch | Non-intrusive liquid level monitoring and alarming device | probes number | non intrusive | AISI 316L | Modbus | -Shell protection level IP67
|  | 2 × MC4, 16 × CC1, (16 × CC2) *** | 34 |  |  | or | - probe dimenions to be provided
|  |  | switch heads |  |  | Serial Interface RS-485 | -probe installation procedures (e.g silicone grease, drying glue & adapters) for:
|  |  | 17 |  |  |  | a. steel tank walls
b. non-ferromagnetic tank walls
7 | Temperature transmitter | Resistance Thermometer assemly with Smart temperature transmitter (liquid gas type) | 2 | 1/2" NPT | AISI 316L | Serial Interface RS-485 | with resistance thermometer assembly
|  | MU1, MU2 with insert length 4920 mm |  |  |  | or | +
[6 empty] | 4-20 mA HART | transmitter
8 | Temperature transmitter | Resistance Thermometer assemly with Smart temperature transmitter (liquid gas type) | 1 | 1/2" NPT | AISI 316L | Serial Interface RS-485 | with resistance thermometer assembly
|  | MC3 with insert length 4120 mm |  |  |  | or | +
[6 empty] | 4-20 mA HART | transmitter
9 | Temperature transmitter | Resistance Thermometer assemly with Smart temperature transmitter (liquid gas type) | 1 | 1/2" NPT | AISI 316L | Serial Interface RS-485 | with resistance thermometer assembly
|  | MC4 with insert length 510 mm |  |  |  | or | +
[6 empty] | 4-20 mA HART | transmitter
10 | Pressure Transmitter | MU1, MU2, MC3, MC4 | 4 | 1/2" NPT | AISI 316L | Serial Interface RS-485 | -Gauge pressure
[6 empty] | or | -mounting bracket
4-20 mA HART
11 | Digital Indicators** | Temperature/Pressure field |  |  |  |  | 4 digit Intrinsicaly safe indicator